{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["数据","Sheet1","4泡沫产生器原始记录2018(1)"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"数据","index":0,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Sheet1","index":1,"n_rows":18,"n_cols":2,"rows_kept":18,"cut":false,"hidden":false,"merged":[[0,0,0,8],[1,1,1,8],[2,1,2,8],[3,1,3,8],[4,1,4,8],[5,1,5,8],[6,1,6,8],[7,1,7,8],[8,1,8,8],[9,1,9,8],[10,1,10,8],[11,0,11,8],[12,0,12,8],[13,1,13,2],[14,1,14,2],[15,1,15,2],[16,1,16,2],[17,1,17,2]]}
["Ⅰ：泡沫产生器常见问题："]
[1,"泡沫产生器密封玻璃破裂。"]
[2,"泡沫产生器紧固部件锈蚀严重，无法拆解维修。"]
[3,"泡沫产生器隔离网脱落或锈蚀损坏，存在鸟窝等异物堵塞喷嘴。"]
[4,"泡沫产生器内部存在锈蚀物或油污，堵塞喷嘴。"]
[5,"泡沫产生器因螺栓锈蚀严重，导致无法拆解和检测。"]
[6,"永久性产品标牌不符合标准要求（新品可作为否定项，在用产品不作为初检不合格否定项）。"]
["7-1","泡沫产生器其他状况："]
["7-2","泡沫产生器其他状况："]
["7-3","泡沫产生器其他状况："]
["7-4","泡沫产生器其他状况："]
[" "]
["Ⅱ：泡沫产生器问题的位置"]
["A","壳体"]
["B","防护罩"]
["C","喷嘴组"]
["D","密封玻璃（阀盘）"]
["E","连接机构"]

{"sheet":"4泡沫产生器原始记录2018(1)","index":2,"n_rows":60,"n_cols":10,"rows_kept":60,"cut":false,"hidden":false,"merged":[[0,0,0,10],[1,1,1,4],[1,5,1,10],[2,1,2,7],[2,8,2,9],[3,1,3,7],[3,8,3,9],[4,0,4,1],[4,2,4,10],[5,0,5,1],[5,2,5,10],[6,1,6,3],[6,5,6,6],[6,7,6,10],[7,1,7,3],[7,5,7,6],[7,7,7,10],[8,2,8,3],[8,7,8,8],[9,2,9,5],[9,7,9,10],[10,1,10,3],[10,5,10,6],[10,7,10,10],[11,1,11,3],[11,5,11,6],[11,7,11,10],[12,2,12,3],[12,7,12,8],[13,2,13,5],[13,7,13,10],[14,1,14,3],[14,5,14,6],[14,7,14,10],[15,1,15,3],[15,5,15,6],[15,7,15,10],[16,2,16,3],[16,7,16,8],[17,2,17,5],[17,7,17,10],[18,1,18,3],[18,5,18,6],[18,7,18,10],[19,1,19,3],[19,5,19,6],[19,7,19,10],[20,2,20,3],[20,7,20,8],[21,2,21,5],[21,7,21,10],[22,1,22,3],[22,5,22,6],[22,7,22,10],[23,1,23,3],[23,5,23,6],[23,7,23,10],[24,2,24,3],[24,7,24,8],[25,2,25,5],[25,7,25,10],[26,0,26,10],[27,0,27,10],[28,0,28,10],[29,0,29,10],[30,0,30,10],[31,1,31,5],[31,7,31,10],[32,0,32,10],[33,0,33,10],[34,0,34,10],[35,0,35,10],[54,0,54,10],[55,0,55,10],[56,0,56,10],[57,0,57,10],[58,0,58,10],[59,0,59,10],[7,0,9,0],[11,0,13,0],[15,0,17,0],[19,0,21,0],[23,0,25,0]]}
["空气泡沫产生器检测数据记录表"]
["编码:  "," J宇Q04.01-",null,null,null,"第     页    共     页"]
["委托单位：",{"$nulls":7},"检测日期："]
["检测地点：",{"$nulls":7},"环境温度： "]
["检测仪器及编号：",null,"压力变送器"]
["依据标准及代号：",null,"GB20031-2005   泡沫灭火系统及部件通用技术条件"]
["序号","安装位置",null,null,"出厂编号","规格型号",null,"制造厂家"]
[]
[null,"供给压力 MPa",null,null,"玻璃破碎压力 MPa",null,"标牌检查",null,null,"易裂线检查"]
[null,"备注1：",{"$nulls":4},"备注2："]
["序号","安装位置",null,null,"出厂编号","规格型号",null,"制造厂家"]
[]
[null,"供给压力 MPa",null,null,"玻璃破碎压力 MPa",null,"标牌检查",null,null,"易裂线检查"]
[null,"备注1：",{"$nulls":4},"备注2："]
["序号","安装位置",null,null,"出厂编号","规格型号",null,"制造厂家"]
[]
[null,"供给压力 MPa",null,null,"玻璃破碎压力 MPa",null,"标牌检查",null,null,"易裂线检查"]
[null,"备注1：",{"$nulls":4},"备注2："]
["序号","安装位置",null,null,"出厂编号","规格型号",null,"制造厂家"]
[]
[null,"供给压力 MPa",null,null,"玻璃破碎压力 MPa",null,"标牌检查",null,null,"易裂线检查"]
[null,"备注1：",{"$nulls":4},"备注2："]
["序号","安装位置",null,null,"出厂编号","规格型号",null,"制造厂家"]
[]
[null,"供给压力 MPa",null,null,"玻璃破碎压力 MPa",null,"标牌检查",null,null,"易裂线检查"]
[null,"备注1：",{"$nulls":4},"备注2："]
["备注3："]
["消防管线检查：渗漏□  锈蚀□  破损□   无定期维修保养□      其他：                                            "]
["消防栓检查：渗漏□  锈蚀□  破损□   无定期维修保养□        其他：                                            "]
["消防阀门检查：渗漏□  锈蚀□  开关失灵□  无定期维修保养□   其他：                                            "]
["泡沫灭火控制系统检查：不能正常启动□   需调试后启动□        其他：                                            "]
["主检人：",{"$nulls":5},"校核人："]
[" "]
[" "]
[" "]
[" "]
{"$rows_empty":18}
[" "]
[" "]
[" "]
[" "]
[" "]
[" "]